## ID A #1
PSYCHROMETRIC CALORIMETER DATA SHEET
Company |  |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  |  | Exp. Device
Model (1) |  |  |  |  | Refrigerant
Serial No. (1) |  |  |  |  | Ref. Charge
Model (2) |  |  |  |  | Test Date |  | 2018-08-17 17:54:05
Serial No. (2) |  |  |  |  | File Name
Model (3) / Serial No. (3) |  | / |  |  | -
Indoor Side Test Condition |  |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 27.00 / 19.00 ℃
Test Record |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Total Results |  | Average | 1 min | 2 min
Total Capacity | kcal/h | 151780.1 | 151780.1 | 151780.1
Total Power Input | W | 11005 | 11005 | 11005
EER/COP | kcal/hW | 13.792 | 13.7919 | 13.7919
Capacity Ratio | % | 0 | 0 | 0
Power Input Ratio | % | 0 | 0 | 0
EER/COP Ratio | % | 0 | 0 | 0
Power Input (ID Unit) | W | 2751.1 | 2751.099 | 2751.099
Voltage | V | 231.1 | 231.0999 | 231.0999
Current | A | 11.001 | 11.001 | 11.001
Frequency | Hz | 61.01 | 61.01 | 61.01
Power Factor | % | 91.01 | 91.0099 | 91.0099
Power Input (OD Unit) | W | 2751.4 | 2751.401 | 2751.401
Voltage | V | 231.4 | 231.4001 | 231.4001
Current | A | 11.004 | 11.004 | 11.004
Frequency | Hz | 61.04 | 61.04 | 61.04
Power Factor | % | 91.04 | 91.04 | 91.04
Indoor Side A #1
Capacity | kcal/h | 58232.2 | 58232.18 | 58232.18
Capacity Ratio | % | 1455803 | 1455803 | 1455803
Sensible Heat | kcal/h | 39221.9 | 39221.89 | 39221.89
Latent Heat | kcal/h | 19010.3 | 19010.25 | 19010.25
Sensible Heat Ratio | % | 67.35 | 67.3543 | 67.3543
Heat Leakage | kcal/h | 112 | 112 | 112
Drain Weight | kg/h | 32.33 | 32.3304 | 32.3304
Entering DB | ℃ | 27.11 | 27.11 | 27.11
Entering WB | ℃ | 19.11 | 19.11 | 19.11
Entering RH | % | 46.87 | 46.87 | 46.87
Leaving DB | ℃ | 11.11 | 11.11 | 11.11
Leaving WB | ℃ | 10.11 | 10.11 | 10.11
Leaving RH | % | 88.25 | 88.2476 | 88.2476
Enthalpy [Ent] | kcal/kg' | 12.935 | 12.9346 | 12.9346
Enthalpy [Lev] | kcal/kg' | 7.048 | 7.0483 | 7.0483
Humidity Ratio [Ent] | kg/kg' | 0.0106 | 0.010551 | 0.010551
Humidity Ratio [Lev] | kg/kg' | 0.0073 | 0.0072765 | 0.0072765
Specific Heat [Lev] | kcal/kg℃ | 0.2432 | 0.24321 | 0.24321
Specific Volume [Lev] | ㎥/kg | 0.8089 | 0.8089 | 0.8089
Air Flow [Lev] | CMM | 134.09 | 134.0858 | 134.0858
Static Pressure | mmAq | 0.11 | 0.11 | 0.11
Nozzle Diff. Pressure | mmAq | 25.11 | 25.11 | 25.11
Atmospheric Pressure | mmHg | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 12.11 | 12.11 | 12.11
Nozzle (100/150/150/300) |  | O,O,O,O
Outdoor Side
Entering DB | ℃ | 35.33 | 35.33 | 35.33
Entering WB | ℃ | 24.33 | 24.33 | 24.33
Entering RH | % | 0 | 0 | 0
Entering DP | ℃ | 10.33 | 10.33 | 10.33
LG-P14-ID.A-TD1 |  |  | LG Electronics |  |  | A4(210mm*297mm)

## ID A #2
PSYCHROMETRIC CALORIMETER DATA SHEET
Company |  |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  |  | Exp. Device
Model (1) |  |  |  |  | Refrigerant
Serial No. (1) |  |  |  |  | Ref. Charge
Model (2) |  |  |  |  | Test Date |  | 2018-08-17 17:54:05
Serial No. (2) |  |  |  |  | File Name
Model (3) / Serial No. (3) |  | / |  |  | -
Indoor Side Test Condition |  |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 27.00 / 19.00 ℃
Test Record |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Total Results |  | Average | 1 min | 2 min
Total Capacity | kcal/h | 151780.1 | 151780.1 | 151780.1
Total Power Input | W | 11005 | 11005 | 11005
EER/COP | kcal/hW | 13.792 | 13.7919 | 13.7919
Capacity Ratio | % | 0 | 0 | 0
Power Input Ratio | % | 0 | 0 | 0
EER/COP Ratio | % | 0 | 0 | 0
Power Input (ID Unit) | W | 2751.1 | 2751.099 | 2751.099
Voltage | V | 231.1 | 231.0999 | 231.0999
Current | A | 11.001 | 11.001 | 11.001
Frequency | Hz | 61.01 | 61.01 | 61.01
Power Factor | % | 91.01 | 91.0099 | 91.0099
Power Input (OD Unit) | W | 2751.4 | 2751.401 | 2751.401
Voltage | V | 231.4 | 231.4001 | 231.4001
Current | A | 11.004 | 11.004 | 11.004
Frequency | Hz | 61.04 | 61.04 | 61.04
Power Factor | % | 91.04 | 91.04 | 91.04
Indoor Side A #2
Capacity | kcal/h | 12345.1 | 12345.1 | 12345.1
Capacity Ratio | % | 308627.3 | 308627.3 | 308627.3
Sensible Heat | kcal/h | 8325.3 | 8325.273 | 8325.273
Latent Heat | kcal/h | 4019.8 | 4019.828 | 4019.828
Sensible Heat Ratio | % | 67.44 | 67.4378 | 67.4378
Heat Leakage | kcal/h | 64 | 64 | 64
Drain Weight | kg/h | 6.84 | 6.8364 | 6.8364
Entering DB | ℃ | 27.12 | 27.12 | 27.12
Entering WB | ℃ | 19.12 | 19.12 | 19.12
Entering RH | % | 46.88 | 46.8808 | 46.8808
Leaving DB | ℃ | 11.12 | 11.12 | 11.12
Leaving WB | ℃ | 10.12 | 10.12 | 10.12
Leaving RH | % | 88.25 | 88.2513 | 88.2513
Enthalpy [Ent] | kcal/kg' | 12.942 | 12.9424 | 12.9424
Enthalpy [Lev] | kcal/kg' | 7.054 | 7.0539 | 7.0539
Humidity Ratio [Ent] | kg/kg' | 0.0106 | 0.01056 | 0.01056
Humidity Ratio [Lev] | kg/kg' | 0.0073 | 0.0072817 | 0.0072817
Specific Heat [Lev] | kcal/kg℃ | 0.2432 | 0.24321 | 0.24321
Specific Volume [Lev] | ㎥/kg | 0.8089 | 0.80893 | 0.80893
Air Flow [Lev] | CMM | 28.32 | 28.3236 | 28.3236
Static Pressure | mmAq | 0.12 | 0.12 | 0.12
Nozzle Diff. Pressure | mmAq | 25.12 | 25.12 | 25.12
Atmospheric Pressure | mmHg | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 12.12 | 12.12 | 12.12
Nozzle (100/60/85/100) |  | O,O,O,O
Outdoor Side
Entering DB | ℃ | 35.33 | 35.33 | 35.33
Entering WB | ℃ | 24.33 | 24.33 | 24.33
Entering RH | % | 0 | 0 | 0
Entering DP | ℃ | 10.33 | 10.33 | 10.33
LG-P14-ID.A-TD2 |  |  | LG Electronics |  |  | A4(210mm*297mm)

## ID B #1
PSYCHROMETRIC CALORIMETER DATA SHEET
Company |  |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  |  | Exp. Device
Model (1) |  |  |  |  | Refrigerant
Serial No. (1) |  |  |  |  | Ref. Charge
Model (2) |  |  |  |  | Test Date |  | 2018-08-17 17:54:05
Serial No. (2) |  |  |  |  | File Name
Model (3) / Serial No. (3) |  | / |  |  | -
Indoor Side Test Condition |  |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 27.00 / 19.00 ℃
Test Record |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Total Results |  | Average | 1 min | 2 min
Total Capacity | kcal/h | 151780.1 | 151780.1 | 151780.1
Total Power Input | W | 11005 | 11005 | 11005
EER/COP | kcal/hW | 13.792 | 13.7919 | 13.7919
Capacity Ratio | % | 0 | 0 | 0
Power Input Ratio | % | 0 | 0 | 0
EER/COP Ratio | % | 0 | 0 | 0
Power Input (ID Unit) | W | 2751.1 | 2751.099 | 2751.099
Voltage | V | 231.1 | 231.0999 | 231.0999
Current | A | 11.001 | 11.001 | 11.001
Frequency | Hz | 61.01 | 61.01 | 61.01
Power Factor | % | 91.01 | 91.0099 | 91.0099
Power Input (OD Unit) | W | 2751.4 | 2751.401 | 2751.401
Voltage | V | 231.4 | 231.4001 | 231.4001
Current | A | 11.004 | 11.004 | 11.004
Frequency | Hz | 61.04 | 61.04 | 61.04
Power Factor | % | 91.04 | 91.04 | 91.04
Indoor Side B #1
Capacity | kcal/h | 57069.5 | 57069.5 | 57069.5
Capacity Ratio | % | 1426736 | 1426736 | 1426736
Sensible Heat | kcal/h | 47722.5 | 47722.51 | 47722.51
Latent Heat | kcal/h | 9346.9 | 9346.944 | 9346.944
Sensible Heat Ratio | % | 83.62 | 83.6218 | 83.6218
Heat Leakage | kcal/h | 160 | 160 | 160
Drain Weight | kg/h | 15.9 | 15.8962 | 15.8962
Entering DB | ℃ | 27.21 | 27.21 | 27.21
Entering WB | ℃ | 19.21 | 19.21 | 19.21
Entering RH | % | 46.98 | 46.9778 | 46.9778
Leaving DB | ℃ | 11.21 | 11.21 | 11.21
Leaving WB | ℃ | 10.21 | 10.21 | 10.21
Leaving RH | % | 88.28 | 88.285 | 88.285
Enthalpy [Ent] | kcal/kg' | 13.013 | 13.0126 | 13.0126
Enthalpy [Lev] | kcal/kg' | 7.104 | 7.1041 | 7.1041
Humidity Ratio [Ent] | kg/kg' | 0.0106 | 0.010639 | 0.010639
Humidity Ratio [Lev] | kg/kg' | 0.0073 | 0.0073287 | 0.0073287
Specific Heat [Lev] | kcal/kg℃ | 0.2432 | 0.24323 | 0.24323
Specific Volume [Lev] | ㎥/kg | 0.8092 | 0.80921 | 0.80921
Air Flow [Lev] | CMM | 65.24 | 65.2429 | 65.2429
Static Pressure | mmAq | 0.21 | 0.21 | 0.21
Nozzle Diff. Pressure | mmAq | 25.21 | 25.21 | 25.21
Atmospheric Pressure | mmHg | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 12.21 | 12.21 | 12.21
Nozzle (100/125/150/150) |  | O,O,O,O
Outdoor Side
Entering DB | ℃ | 35.33 | 35.33 | 35.33
Entering WB | ℃ | 24.33 | 24.33 | 24.33
Entering RH | % | 0 | 0 | 0
Entering DP | ℃ | 10.33 | 10.33 | 10.33
LG-P14-ID.B-TD1 |  |  | LG Electronics |  |  | A4(210mm*297mm)

## ID B #2
PSYCHROMETRIC CALORIMETER DATA SHEET
Company |  |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  |  | Exp. Device
Model (1) |  |  |  |  | Refrigerant
Serial No. (1) |  |  |  |  | Ref. Charge
Model (2) |  |  |  |  | Test Date |  | 2018-08-17 17:54:05
Serial No. (2) |  |  |  |  | File Name
Model (3) / Serial No. (3) |  | / |  |  | -
Indoor Side Test Condition |  |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 27.00 / 19.00 ℃
Test Record |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Total Results |  | Average | 1 min | 2 min
Total Capacity | kcal/h | 151780.1 | 151780.1 | 151780.1
Total Power Input | W | 11005 | 11005 | 11005
EER/COP | kcal/hW | 13.792 | 13.7919 | 13.7919
Capacity Ratio | % | 0 | 0 | 0
Power Input Ratio | % | 0 | 0 | 0
EER/COP Ratio | % | 0 | 0 | 0
Power Input (ID Unit) | W | 2751.1 | 2751.099 | 2751.099
Voltage | V | 231.1 | 231.0999 | 231.0999
Current | A | 11.001 | 11.001 | 11.001
Frequency | Hz | 61.01 | 61.01 | 61.01
Power Factor | % | 91.01 | 91.0099 | 91.0099
Power Input (OD Unit) | W | 2751.4 | 2751.401 | 2751.401
Voltage | V | 231.4 | 231.4001 | 231.4001
Current | A | 11.004 | 11.004 | 11.004
Frequency | Hz | 61.04 | 61.04 | 61.04
Power Factor | % | 91.04 | 91.04 | 91.04
Indoor Side B #2
Capacity | kcal/h | 24133.5 | 24133.46 | 24133.46
Capacity Ratio | % | 603336.4 | 603336.4 | 603336.4
Sensible Heat | kcal/h | 16214.9 | 16214.94 | 16214.94
Latent Heat | kcal/h | 7918.5 | 7918.523 | 7918.523
Sensible Heat Ratio | % | 67.19 | 67.1887 | 67.1887
Heat Leakage | kcal/h | 112 | 112 | 112
Drain Weight | kg/h | 13.47 | 13.4669 | 13.4669
Entering DB | ℃ | 27.22 | 27.22 | 27.22
Entering WB | ℃ | 19.22 | 19.22 | 19.22
Entering RH | % | 46.99 | 46.9885 | 46.9885
Leaving DB | ℃ | 11.22 | 11.22 | 11.22
Leaving WB | ℃ | 10.22 | 10.22 | 10.22
Leaving RH | % | 88.29 | 88.2886 | 88.2886
Enthalpy [Ent] | kcal/kg' | 13.02 | 13.0205 | 13.0205
Enthalpy [Lev] | kcal/kg' | 7.11 | 7.1097 | 7.1097
Humidity Ratio [Ent] | kg/kg' | 0.0106 | 0.010648 | 0.010648
Humidity Ratio [Lev] | kg/kg' | 0.0073 | 0.0073339 | 0.0073339
Specific Heat [Lev] | kcal/kg℃ | 0.2432 | 0.24323 | 0.24323
Specific Volume [Lev] | ㎥/kg | 0.8092 | 0.80924 | 0.80924
Air Flow [Lev] | CMM | 55.21 | 55.2148 | 55.2148
Static Pressure | mmAq | 0.22 | 0.22 | 0.22
Nozzle Diff. Pressure | mmAq | 25.22 | 25.22 | 25.22
Atmospheric Pressure | mmHg | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 12.22 | 12.22 | 12.22
Nozzle (50/200/85/100) |  | O,O,O,O
Outdoor Side
Entering DB | ℃ | 35.33 | 35.33 | 35.33
Entering WB | ℃ | 24.33 | 24.33 | 24.33
Entering RH | % | 0 | 0 | 0
Entering DP | ℃ | 10.33 | 10.33 | 10.33
LG-P14-ID.B-TD2 |  |  | LG Electronics |  |  | A4(210mm*297mm)

## ID A TC
THERMOCOUPLE DATA SHEET
Company | [5 empty] | Rated Capacity |  | 0.0 kcal/h
Test Name | [5 empty] | Rated Power Input |  | 0.0 W
Test No. | [5 empty] | Rated EER/COP |  | 0.000 kcal/hW
Observer | [5 empty] | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker | [5 empty] | Exp. Device
Model (1) | [5 empty] | Refrigerant
Serial No. (1) | [5 empty] | Ref. Charge
Model (2) | [5 empty] | Test Date |  | 2018-08-17 17:54:05
Serial No. (2) | [5 empty] | File Name
Model (3) / Serial No. (3) |  |  | / |  |  | -
Indoor Side Test Condition | [5 empty] | Outdoor Side Test Condition
DB & WB Temperature |  |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 27.00 / 19.00 ℃
Test Record |  |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Thermocouple |  |  | Average | 1 min | 2 min
Indoor Side A
[01] : | TC 01 | ℃ | 101 | 101 | 101
[02] : | TC 02 | ℃ | 102 | 102 | 102
[03] : | TC 03 | ℃ | 103 | 103 | 103
[04] : | TC 04 | ℃ | 104 | 104 | 104
[05] : | TC 05 | ℃ | 105 | 105 | 105
[06] : | TC 06 | ℃ | 106 | 106 | 106
[07] : | TC 07 | ℃ | 107 | 107 | 107
[08] : | TC 08 | ℃ | 108 | 108 | 108
[09] : | TC 09 | ℃ | 109 | 109 | 109
[10] : | TC 10 | ℃ | 110 | 110 | 110
[11] : | TC 11 | ℃ | 111 | 111 | 111
[12] : | TC 12 | ℃ | 112 | 112 | 112
[13] : | TC 13 | ℃ | 113 | 113 | 113
[14] : | TC 14 | ℃ | 114 | 114 | 114
[15] : | TC 15 | ℃ | 115 | 115 | 115
[16] : | TC 16 | ℃ | 116 | 116 | 116
[17] : | TC 17 | ℃ | 117 | 117 | 117
[18] : | TC 18 | ℃ | 118 | 118 | 118
[19] : | TC 19 | ℃ | 119 | 119 | 119
[20] : | TC 20 | ℃ | 120 | 120 | 120
[21] : | TC 21 | ℃ | 121 | 121 | 121
[22] : | TC 22 | ℃ | 122 | 122 | 122
[23] : | TC 23 | ℃ | 123 | 123 | 123
[24] : | TC 24 | ℃ | 124 | 124 | 124
[25] : | TC 25 | ℃ | 125 | 125 | 125
[26] : | TC 26 | ℃ | 126 | 126 | 126
[27] : | TC 27 | ℃ | 127 | 127 | 127
[28] : | TC 28 | ℃ | 128 | 128 | 128
[29] : | TC 29 | ℃ | 129 | 129 | 129
[30] : | TC 30 | ℃ | 130 | 130 | 130
[31] : | TC 31 | ℃ | 131 | 131 | 131
[32] : | TC 32 | ℃ | 132 | 132 | 132
[33] : | TC 33 | ℃ | 133 | 133 | 133
[34] : | TC 34 | ℃ | 134 | 134 | 134
[35] : | TC 35 | ℃ | 135 | 135 | 135
[36] : | TC 36 | ℃ | 136 | 136 | 136
[37] : | TC 37 | ℃ | 137 | 137 | 137
[38] : | TC 38 | ℃ | 138 | 138 | 138
[39] : | TC 39 | ℃ | 139 | 139 | 139
[40] : | TC 40 | ℃ | 140 | 140 | 140
[41] : | TC 41 | ℃ | 141 | 141 | 141
[42] : | TC 42 | ℃ | 142 | 142 | 142
[43] : | TC 43 | ℃ | 143 | 143 | 143
[44] : | TC 44 | ℃ | 144 | 144 | 144
[45] : | TC 45 | ℃ | 145 | 145 | 145
[46] : | TC 46 | ℃ | 146 | 146 | 146
[47] : | TC 47 | ℃ | 147 | 147 | 147
[48] : | TC 48 | ℃ | 148 | 148 | 148
[49] : | TC 49 | ℃ | 149 | 149 | 149
[50] : | TC 50 | ℃ | 150 | 150 | 150
[51] : | TC 51 | ℃ | 151 | 151 | 151
[52] : | TC 52 | ℃ | 152 | 152 | 152
[53] : | TC 53 | ℃ | 153 | 153 | 153
[54] : | TC 54 | ℃ | 154 | 154 | 154
[55] : | TC 55 | ℃ | 155 | 155 | 155
[56] : | TC 56 | ℃ | 156 | 156 | 156
[57] : | TC 57 | ℃ | 157 | 157 | 157
[58] : | TC 58 | ℃ | 158 | 158 | 158
[59] : | TC 59 | ℃ | 159 | 159 | 159
[60] : | TC 60 | ℃ | 160 | 160 | 160
LG-P14-ID.A-TC |  |  |  | LG Electronics |  |  | A4(210mm*297mm)

## ID B TC
THERMOCOUPLE DATA SHEET
Company | [5 empty] | Rated Capacity |  | 0.0 kcal/h
Test Name | [5 empty] | Rated Power Input |  | 0.0 W
Test No. | [5 empty] | Rated EER/COP |  | 0.000 kcal/hW
Observer | [5 empty] | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker | [5 empty] | Exp. Device
Model (1) | [5 empty] | Refrigerant
Serial No. (1) | [5 empty] | Ref. Charge
Model (2) | [5 empty] | Test Date |  | 2018-08-17 17:54:05
Serial No. (2) | [5 empty] | File Name
Model (3) / Serial No. (3) |  |  | / |  |  | -
Indoor Side Test Condition | [5 empty] | Outdoor Side Test Condition
DB & WB Temperature |  |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 27.00 / 19.00 ℃
Test Record |  |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Thermocouple |  |  | Average | 1 min | 2 min
Indoor Side B
[01] : | TC 01 | ℃ | 201 | 201 | 201
[02] : | TC 02 | ℃ | 202 | 202 | 202
[03] : | TC 03 | ℃ | 203 | 203 | 203
[04] : | TC 04 | ℃ | 204 | 204 | 204
[05] : | TC 05 | ℃ | 205 | 205 | 205
[06] : | TC 06 | ℃ | 206 | 206 | 206
[07] : | TC 07 | ℃ | 207 | 207 | 207
[08] : | TC 08 | ℃ | 208 | 208 | 208
[09] : | TC 09 | ℃ | 209 | 209 | 209
[10] : | TC 10 | ℃ | 210 | 210 | 210
[11] : | TC 11 | ℃ | 211 | 211 | 211
[12] : | TC 12 | ℃ | 212 | 212 | 212
[13] : | TC 13 | ℃ | 213 | 213 | 213
[14] : | TC 14 | ℃ | 214 | 214 | 214
[15] : | TC 15 | ℃ | 215 | 215 | 215
[16] : | TC 16 | ℃ | 216 | 216 | 216
[17] : | TC 17 | ℃ | 217 | 217 | 217
[18] : | TC 18 | ℃ | 218 | 218 | 218
[19] : | TC 19 | ℃ | 219 | 219 | 219
[20] : | TC 20 | ℃ | 220 | 220 | 220
[21] : | TC 21 | ℃ | 221 | 221 | 221
[22] : | TC 22 | ℃ | 222 | 222 | 222
[23] : | TC 23 | ℃ | 223 | 223 | 223
[24] : | TC 24 | ℃ | 224 | 224 | 224
[25] : | TC 25 | ℃ | 225 | 225 | 225
[26] : | TC 26 | ℃ | 226 | 226 | 226
[27] : | TC 27 | ℃ | 227 | 227 | 227
[28] : | TC 28 | ℃ | 228 | 228 | 228
[29] : | TC 29 | ℃ | 229 | 229 | 229
[30] : | TC 30 | ℃ | 230 | 230 | 230
[31] : | TC 31 | ℃ | 231 | 231 | 231
[32] : | TC 32 | ℃ | 232 | 232 | 232
[33] : | TC 33 | ℃ | 233 | 233 | 233
[34] : | TC 34 | ℃ | 234 | 234 | 234
[35] : | TC 35 | ℃ | 235 | 235 | 235
[36] : | TC 36 | ℃ | 236 | 236 | 236
[37] : | TC 37 | ℃ | 237 | 237 | 237
[38] : | TC 38 | ℃ | 238 | 238 | 238
[39] : | TC 39 | ℃ | 239 | 239 | 239
[40] : | TC 40 | ℃ | 240 | 240 | 240
[41] : | TC 41 | ℃ | 241 | 241 | 241
[42] : | TC 42 | ℃ | 242 | 242 | 242
[43] : | TC 43 | ℃ | 243 | 243 | 243
[44] : | TC 44 | ℃ | 244 | 244 | 244
[45] : | TC 45 | ℃ | 245 | 245 | 245
[46] : | TC 46 | ℃ | 246 | 246 | 246
[47] : | TC 47 | ℃ | 247 | 247 | 247
[48] : | TC 48 | ℃ | 248 | 248 | 248
[49] : | TC 49 | ℃ | 249 | 249 | 249
[50] : | TC 50 | ℃ | 250 | 250 | 250
[51] : | TC 51 | ℃ | 251 | 251 | 251
[52] : | TC 52 | ℃ | 252 | 252 | 252
[53] : | TC 53 | ℃ | 253 | 253 | 253
[54] : | TC 54 | ℃ | 254 | 254 | 254
[55] : | TC 55 | ℃ | 255 | 255 | 255
[56] : | TC 56 | ℃ | 256 | 256 | 256
[57] : | TC 57 | ℃ | 257 | 257 | 257
[58] : | TC 58 | ℃ | 258 | 258 | 258
[59] : | TC 59 | ℃ | 259 | 259 | 259
[60] : | TC 60 | ℃ | 260 | 260 | 260
LG-P14-ID.B-TC |  |  |  | LG Electronics |  |  | A4(210mm*297mm)

## OD TC
THERMOCOUPLE DATA SHEET
Company | [5 empty] | Rated Capacity |  | 0.0 kcal/h
Test Name | [5 empty] | Rated Power Input |  | 0.0 W
Test No. | [5 empty] | Rated EER/COP |  | 0.000 kcal/hW
Observer | [5 empty] | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker | [5 empty] | Exp. Device
Model (1) | [5 empty] | Refrigerant
Serial No. (1) | [5 empty] | Ref. Charge
Model (2) | [5 empty] | Test Date |  | 2018-08-17 17:54:05
Serial No. (2) | [5 empty] | File Name
Model (3) / Serial No. (3) |  |  | / |  |  | -
Indoor Side Test Condition | [5 empty] | Outdoor Side Test Condition
DB & WB Temperature |  |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 27.00 / 19.00 ℃
Test Record |  |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Thermocouple |  |  | Average | 1 min | 2 min
Outdoor Side
[01] : | TC 01 | ℃ | 301 | 301 | 301
[02] : | TC 02 | ℃ | 302 | 302 | 302
[03] : | TC 03 | ℃ | 303 | 303 | 303
[04] : | TC 04 | ℃ | 304 | 304 | 304
[05] : | TC 05 | ℃ | 305 | 305 | 305
[06] : | TC 06 | ℃ | 306 | 306 | 306
[07] : | TC 07 | ℃ | 307 | 307 | 307
[08] : | TC 08 | ℃ | 308 | 308 | 308
[09] : | TC 09 | ℃ | 309 | 309 | 309
[10] : | TC 10 | ℃ | 310 | 310 | 310
[11] : | TC 11 | ℃ | 311 | 311 | 311
[12] : | TC 12 | ℃ | 312 | 312 | 312
[13] : | TC 13 | ℃ | 313 | 313 | 313
[14] : | TC 14 | ℃ | 314 | 314 | 314
[15] : | TC 15 | ℃ | 315 | 315 | 315
[16] : | TC 16 | ℃ | 316 | 316 | 316
[17] : | TC 17 | ℃ | 317 | 317 | 317
[18] : | TC 18 | ℃ | 318 | 318 | 318
[19] : | TC 19 | ℃ | 319 | 319 | 319
[20] : | TC 20 | ℃ | 320 | 320 | 320
[21] : | TC 21 | ℃ | 321 | 321 | 321
[22] : | TC 22 | ℃ | 322 | 322 | 322
[23] : | TC 23 | ℃ | 323 | 323 | 323
[24] : | TC 24 | ℃ | 324 | 324 | 324
[25] : | TC 25 | ℃ | 325 | 325 | 325
[26] : | TC 26 | ℃ | 326 | 326 | 326
[27] : | TC 27 | ℃ | 327 | 327 | 327
[28] : | TC 28 | ℃ | 328 | 328 | 328
[29] : | TC 29 | ℃ | 329 | 329 | 329
[30] : | TC 30 | ℃ | 330 | 330 | 330
[31] : | TC 31 | ℃ | 331 | 331 | 331
[32] : | TC 32 | ℃ | 332 | 332 | 332
[33] : | TC 33 | ℃ | 333 | 333 | 333
[34] : | TC 34 | ℃ | 334 | 334 | 334
[35] : | TC 35 | ℃ | 335 | 335 | 335
[36] : | TC 36 | ℃ | 336 | 336 | 336
[37] : | TC 37 | ℃ | 337 | 337 | 337
[38] : | TC 38 | ℃ | 338 | 338 | 338
[39] : | TC 39 | ℃ | 339 | 339 | 339
[40] : | TC 40 | ℃ | 340 | 340 | 340
[41] : | TC 41 | ℃ | 341 | 341 | 341
[42] : | TC 42 | ℃ | 342 | 342 | 342
[43] : | TC 43 | ℃ | 343 | 343 | 343
[44] : | TC 44 | ℃ | 344 | 344 | 344
[45] : | TC 45 | ℃ | 345 | 345 | 345
[46] : | TC 46 | ℃ | 346 | 346 | 346
[47] : | TC 47 | ℃ | 347 | 347 | 347
[48] : | TC 48 | ℃ | 348 | 348 | 348
[49] : | TC 49 | ℃ | 349 | 349 | 349
[50] : | TC 50 | ℃ | 350 | 350 | 350
[51] : | TC 51 | ℃ | 351 | 351 | 351
[52] : | TC 52 | ℃ | 352 | 352 | 352
[53] : | TC 53 | ℃ | 353 | 353 | 353
[54] : | TC 54 | ℃ | 354 | 354 | 354
[55] : | TC 55 | ℃ | 355 | 355 | 355
[56] : | TC 56 | ℃ | 356 | 356 | 356
[57] : | TC 57 | ℃ | 357 | 357 | 357
[58] : | TC 58 | ℃ | 358 | 358 | 358
[59] : | TC 59 | ℃ | 359 | 359 | 359
[60] : | TC 60 | ℃ | 360 | 360 | 360
LG-P14-OD-TC |  |  |  | LG Electronics |  |  | A4(210mm*297mm)

## Raw Data (hidden)
File Name
Test Date
Test Start time
Test End time
ID1 DB & WB
ID1 Test Record
OD DB & WB
OD Test Record
ID2 DB & WB
ID2 Test Record
OD DB & WB
OD Test Record
ID DB & WB
ID Test Record
OD DB & WB
OD Test Record
ID3 DB & WB
ID3 Test Record
OD DB & WB
OD Test Record
ID4 DB & WB
ID4 Test Record
OD DB & WB
OD Test Record
ID1 DB & WB
ID1 Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
ID2 DB & WB
ID2 Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
OD DB & WB
OD Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
ID3 DB & WB
ID3 Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
ID4 DB & WB
ID4 Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
ID DB & WB
ID Test Record
OD DB & WB
OD Test Record
Company
Test Name
Test No.
Observer
Rated Capacity
Rated Power Input
Rated EER/COP
Power Source
Maker
Model 1
Serial No. 1
Model 2
Serial No. 2
Model 3
Serial No. 3
Exp. Device
Refrigerant
Ref. Charge
Memo