## ID A #1
PSYCHROMETRIC CALORIMETER DATA SHEET
Company |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  | Exp. Device
Model (1) |  |  |  | Refrigerant
Serial No. (1) |  |  |  | Ref. Charge
Model (2) |  |  |  | Test Date |  | 2018-09-06 11:08:02
Serial No. (2) |  |  |  | File Name
Model (3) / Serial No. (3) |  | / |  | -
Indoor Side Test Condition |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  | 27.00 / 19.00 ℃ |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  | Cooling, Indoor |  | Test Record |  | Outdoor
Memo
Total Results |  | Current | 1 min
Total Capacity | kcal/h | 151492.1875
Total Power Input | W | 11005
EER/COP | kcal/hW | 13.7658
Capacity Ratio | % | 0
Power Input Ratio | % | 0
EER/COP Ratio | % | 0
Power Input (ID Unit) | W | 2751.1001
Voltage | V | 231.1
Current | A | 11.001
Frequency | Hz | 61.01
Power Factor | % | 91.01
Power Input (OD Unit) | W | 2751.3999
Voltage | V | 231.4
Current | A | 11.004
Frequency | Hz | 61.04
Power Factor | % | 91.04
Indoor Side A #1
Capacity | kcal/h | 58184.1562
Capacity Ratio | % | 0
Sensible Heat | kcal/h | 39173.8945
Latent Heat | kcal/h | 19010.2617
Sensible Heat Ratio | % | 67.3274
Heat Leakage | kcal/h | 64
Drain Weight | kg/h | 32.3304
Entering DB | ℃ | 27.11
Entering WB | ℃ | 19.11
Entering RH | % | 46.87
Leaving DB | ℃ | 11.11
Leaving WB | ℃ | 10.11
Leaving RH | % | 88.2476
Enthalpy [Ent] | kcal/kg' | 12.9346
Enthalpy [Lev] | kcal/kg' | 7.0483
Humidity Ratio [Ent] | kg/kg' | 0.010551
Humidity Ratio [Lev] | kg/kg' | 0.0072765
Specific Heat [Lev] | kcal/kg℃ | 0.24321
Specific Volume [Lev] | ㎥/kg | 0.8089
Air Flow [Lev] | CMM | 134.0858
Static Pressure | mmAq | 0.11
Nozzle Diff. Pressure | mmAq | 25.11
Atmospheric Pressure | mmHg | 760
Nozzle Inlet Temp. | ℃ | 12.11
Nozzle (100/150/150/300) |  | O,O,O,O
Outdoor Side
Entering DB | ℃ | 35.33
Entering WB | ℃ | 24.33
Entering RH | % | 40.4284
Entering DP | ℃ | 19.9234
LG-P14-ID.A-TD1 |  |  | LG Electronics |  | A4(210mm*297mm)

## ID A #2
PSYCHROMETRIC CALORIMETER DATA SHEET
Company |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  | Exp. Device
Model (1) |  |  |  | Refrigerant
Serial No. (1) |  |  |  | Ref. Charge
Model (2) |  |  |  | Test Date |  | 2018-09-06 11:08:02
Serial No. (2) |  |  |  | File Name
Model (3) / Serial No. (3) |  | / |  | -
Indoor Side Test Condition |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  | 27.00 / 19.00 ℃ |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  | Cooling, Indoor |  | Test Record |  | Outdoor
Memo
Total Results |  | Current | 1 min
Total Capacity | kcal/h | 151492.1875
Total Power Input | W | 11005
EER/COP | kcal/hW | 13.7658
Capacity Ratio | % | 0
Power Input Ratio | % | 0
EER/COP Ratio | % | 0
Power Input (ID Unit) | W | 2751.1001
Voltage | V | 231.1
Current | A | 11.001
Frequency | Hz | 61.01
Power Factor | % | 91.01
Power Input (OD Unit) | W | 2751.3999
Voltage | V | 231.4
Current | A | 11.004
Frequency | Hz | 61.04
Power Factor | % | 91.04
Indoor Side A #2
Capacity | kcal/h | 12345.0947
Capacity Ratio | % | 0
Sensible Heat | kcal/h | 8325.2676
Latent Heat | kcal/h | 4019.8276
Sensible Heat Ratio | % | 67.4379
Heat Leakage | kcal/h | 64
Drain Weight | kg/h | 6.8364
Entering DB | ℃ | 27.12
Entering WB | ℃ | 19.12
Entering RH | % | 46.8808
Leaving DB | ℃ | 11.12
Leaving WB | ℃ | 10.12
Leaving RH | % | 88.2513
Enthalpy [Ent] | kcal/kg' | 12.9424
Enthalpy [Lev] | kcal/kg' | 7.0539
Humidity Ratio [Ent] | kg/kg' | 0.01056
Humidity Ratio [Lev] | kg/kg' | 0.0072817
Specific Heat [Lev] | kcal/kg℃ | 0.24321
Specific Volume [Lev] | ㎥/kg | 0.80893
Air Flow [Lev] | CMM | 28.3235
Static Pressure | mmAq | 0.12
Nozzle Diff. Pressure | mmAq | 25.12
Atmospheric Pressure | mmHg | 760
Nozzle Inlet Temp. | ℃ | 12.12
Nozzle (100/60/85/100) |  | O,O,O,O
Outdoor Side
Entering DB | ℃ | 35.33
Entering WB | ℃ | 24.33
Entering RH | % | 40.4284
Entering DP | ℃ | 19.9234
LG-P14-ID.A-TD2 |  |  | LG Electronics |  | A4(210mm*297mm)

## ID B #1
PSYCHROMETRIC CALORIMETER DATA SHEET
Company |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  | Exp. Device
Model (1) |  |  |  | Refrigerant
Serial No. (1) |  |  |  | Ref. Charge
Model (2) |  |  |  | Test Date |  | 2018-09-06 11:08:02
Serial No. (2) |  |  |  | File Name
Model (3) / Serial No. (3) |  | / |  | -
Indoor Side Test Condition |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  | 27.00 / 19.00 ℃ |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  | Cooling, Indoor |  | Test Record |  | Outdoor
Memo
Total Results |  | Current | 1 min
Total Capacity | kcal/h | 151492.1875
Total Power Input | W | 11005
EER/COP | kcal/hW | 13.7658
Capacity Ratio | % | 0
Power Input Ratio | % | 0
EER/COP Ratio | % | 0
Power Input (ID Unit) | W | 2751.1001
Voltage | V | 231.1
Current | A | 11.001
Frequency | Hz | 61.01
Power Factor | % | 91.01
Power Input (OD Unit) | W | 2751.3999
Voltage | V | 231.4
Current | A | 11.004
Frequency | Hz | 61.04
Power Factor | % | 91.04
Indoor Side B #1
Capacity | kcal/h | 56877.4766
Capacity Ratio | % | 0
Sensible Heat | kcal/h | 47530.5234
Latent Heat | kcal/h | 9346.9531
Sensible Heat Ratio | % | 83.5665
Heat Leakage | kcal/h | 64
Drain Weight | kg/h | 15.8962
Entering DB | ℃ | 27.21
Entering WB | ℃ | 19.21
Entering RH | % | 46.9777
Leaving DB | ℃ | 11.21
Leaving WB | ℃ | 10.21
Leaving RH | % | 88.2849
Enthalpy [Ent] | kcal/kg' | 13.0126
Enthalpy [Lev] | kcal/kg' | 7.1041
Humidity Ratio [Ent] | kg/kg' | 0.010639
Humidity Ratio [Lev] | kg/kg' | 0.0073287
Specific Heat [Lev] | kcal/kg℃ | 0.24323
Specific Volume [Lev] | ㎥/kg | 0.80921
Air Flow [Lev] | CMM | 65.2429
Static Pressure | mmAq | 0.21
Nozzle Diff. Pressure | mmAq | 25.21
Atmospheric Pressure | mmHg | 760
Nozzle Inlet Temp. | ℃ | 12.21
Nozzle (100/125/150/150) |  | O,O,O,O
Outdoor Side
Entering DB | ℃ | 35.33
Entering WB | ℃ | 24.33
Entering RH | % | 40.4284
Entering DP | ℃ | 19.9234
LG-P14-ID.B-TD1 |  |  | LG Electronics |  | A4(210mm*297mm)

## ID B #2
PSYCHROMETRIC CALORIMETER DATA SHEET
Company |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  | Exp. Device
Model (1) |  |  |  | Refrigerant
Serial No. (1) |  |  |  | Ref. Charge
Model (2) |  |  |  | Test Date |  | 2018-09-06 11:08:02
Serial No. (2) |  |  |  | File Name
Model (3) / Serial No. (3) |  | / |  | -
Indoor Side Test Condition |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  | 27.00 / 19.00 ℃ |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  | Cooling, Indoor |  | Test Record |  | Outdoor
Memo
Total Results |  | Current | 1 min
Total Capacity | kcal/h | 151492.1875
Total Power Input | W | 11005
EER/COP | kcal/hW | 13.7658
Capacity Ratio | % | 0
Power Input Ratio | % | 0
EER/COP Ratio | % | 0
Power Input (ID Unit) | W | 2751.1001
Voltage | V | 231.1
Current | A | 11.001
Frequency | Hz | 61.01
Power Factor | % | 91.01
Power Input (OD Unit) | W | 2751.3999
Voltage | V | 231.4
Current | A | 11.004
Frequency | Hz | 61.04
Power Factor | % | 91.04
Indoor Side B #2
Capacity | kcal/h | 24085.4668
Capacity Ratio | % | 0
Sensible Heat | kcal/h | 16166.9492
Latent Heat | kcal/h | 7918.5171
Sensible Heat Ratio | % | 67.1233
Heat Leakage | kcal/h | 64
Drain Weight | kg/h | 13.4669
Entering DB | ℃ | 27.22
Entering WB | ℃ | 19.22
Entering RH | % | 46.9885
Leaving DB | ℃ | 11.22
Leaving WB | ℃ | 10.22
Leaving RH | % | 88.2886
Enthalpy [Ent] | kcal/kg' | 13.0205
Enthalpy [Lev] | kcal/kg' | 7.1097
Humidity Ratio [Ent] | kg/kg' | 0.010648
Humidity Ratio [Lev] | kg/kg' | 0.0073339
Specific Heat [Lev] | kcal/kg℃ | 0.24323
Specific Volume [Lev] | ㎥/kg | 0.80924
Air Flow [Lev] | CMM | 55.2148
Static Pressure | mmAq | 0.22
Nozzle Diff. Pressure | mmAq | 25.22
Atmospheric Pressure | mmHg | 760
Nozzle Inlet Temp. | ℃ | 12.22
Nozzle (50/200/85/100) |  | O,O,O,O
Outdoor Side
Entering DB | ℃ | 35.33
Entering WB | ℃ | 24.33
Entering RH | % | 40.4284
Entering DP | ℃ | 19.9234
LG-P14-ID.B-TD2 |  |  | LG Electronics |  | A4(210mm*297mm)

## ID A TC
THERMOCOUPLE DATA SHEET
Company |  |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  |  | Exp. Device
Model (1) |  |  |  |  | Refrigerant
Serial No. (1) |  |  |  |  | Ref. Charge
Model (2) |  |  |  |  | Test Date |  | 2018-09-06 11:08:02
Serial No. (2) |  |  |  |  | File Name
Model (3) / Serial No. (3) |  |  | / |  | -
Indoor Side Test Condition |  |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  |  | 27.00 / 19.00 ℃ |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  |  | Cooling, Indoor |  | Test Record |  | Outdoor
Memo
Thermocouple |  |  | Current | 1 min
Indoor Side A
[01] : | TC 01 | ℃ | 101
[02] : | TC 02 | ℃ | 102
[03] : | TC 03 | ℃ | 103
[04] : | TC 04 | ℃ | 104
[05] : | TC 05 | ℃ | 105
[06] : | TC 06 | ℃ | 106
[07] : | TC 07 | ℃ | 107
[08] : | TC 08 | ℃ | 108
[09] : | TC 09 | ℃ | 109
[10] : | TC 10 | ℃ | 110
[11] : | TC 11 | ℃ | 111
[12] : | TC 12 | ℃ | 112
[13] : | TC 13 | ℃ | 113
[14] : | TC 14 | ℃ | 114
[15] : | TC 15 | ℃ | 115
[16] : | TC 16 | ℃ | 116
[17] : | TC 17 | ℃ | 117
[18] : | TC 18 | ℃ | 118
[19] : | TC 19 | ℃ | 119
[20] : | TC 20 | ℃ | 120
[21] : | TC 21 | ℃ | 121
[22] : | TC 22 | ℃ | 122
[23] : | TC 23 | ℃ | 123
[24] : | TC 24 | ℃ | 124
[25] : | TC 25 | ℃ | 125
[26] : | TC 26 | ℃ | 126
[27] : | TC 27 | ℃ | 127
[28] : | TC 28 | ℃ | 128
[29] : | TC 29 | ℃ | 129
[30] : | TC 30 | ℃ | 130
[31] : | TC 31 | ℃ | 131
[32] : | TC 32 | ℃ | 132
[33] : | TC 33 | ℃ | 133
[34] : | TC 34 | ℃ | 134
[35] : | TC 35 | ℃ | 135
[36] : | TC 36 | ℃ | 136
[37] : | TC 37 | ℃ | 137
[38] : | TC 38 | ℃ | 138
[39] : | TC 39 | ℃ | 139
[40] : | TC 40 | ℃ | 140
[41] : | TC 41 | ℃ | 141
[42] : | TC 42 | ℃ | 142
[43] : | TC 43 | ℃ | 143
[44] : | TC 44 | ℃ | 144
[45] : | TC 45 | ℃ | 145
[46] : | TC 46 | ℃ | 146
[47] : | TC 47 | ℃ | 147
[48] : | TC 48 | ℃ | 148
[49] : | TC 49 | ℃ | 149
[50] : | TC 50 | ℃ | 150
[51] : | TC 51 | ℃ | 151
[52] : | TC 52 | ℃ | 152
[53] : | TC 53 | ℃ | 153
[54] : | TC 54 | ℃ | 154
[55] : | TC 55 | ℃ | 155
[56] : | TC 56 | ℃ | 156
[57] : | TC 57 | ℃ | 157
[58] : | TC 58 | ℃ | 158
[59] : | TC 59 | ℃ | 159
[60] : | TC 60 | ℃ | 160
LG-P14-ID.A-TC |  |  |  | LG Electronics |  | A4(210mm*297mm)

## ID B TC
THERMOCOUPLE DATA SHEET
Company |  |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  |  | Exp. Device
Model (1) |  |  |  |  | Refrigerant
Serial No. (1) |  |  |  |  | Ref. Charge
Model (2) |  |  |  |  | Test Date |  | 2018-09-06 11:08:02
Serial No. (2) |  |  |  |  | File Name
Model (3) / Serial No. (3) |  |  | / |  | -
Indoor Side Test Condition |  |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  |  | 27.00 / 19.00 ℃ |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  |  | Cooling, Indoor |  | Test Record |  | Outdoor
Memo
Thermocouple |  |  | Current | 1 min
Indoor Side B
[01] : | TC 01 | ℃ | 201
[02] : | TC 02 | ℃ | 202
[03] : | TC 03 | ℃ | 203
[04] : | TC 04 | ℃ | 204
[05] : | TC 05 | ℃ | 205
[06] : | TC 06 | ℃ | 206
[07] : | TC 07 | ℃ | 207
[08] : | TC 08 | ℃ | 208
[09] : | TC 09 | ℃ | 209
[10] : | TC 10 | ℃ | 210
[11] : | TC 11 | ℃ | 211
[12] : | TC 12 | ℃ | 212
[13] : | TC 13 | ℃ | 213
[14] : | TC 14 | ℃ | 214
[15] : | TC 15 | ℃ | 215
[16] : | TC 16 | ℃ | 216
[17] : | TC 17 | ℃ | 217
[18] : | TC 18 | ℃ | 218
[19] : | TC 19 | ℃ | 219
[20] : | TC 20 | ℃ | 220
[21] : | TC 21 | ℃ | 221
[22] : | TC 22 | ℃ | 222
[23] : | TC 23 | ℃ | 223
[24] : | TC 24 | ℃ | 224
[25] : | TC 25 | ℃ | 225
[26] : | TC 26 | ℃ | 226
[27] : | TC 27 | ℃ | 227
[28] : | TC 28 | ℃ | 228
[29] : | TC 29 | ℃ | 229
[30] : | TC 30 | ℃ | 230
[31] : | TC 31 | ℃ | 231
[32] : | TC 32 | ℃ | 232
[33] : | TC 33 | ℃ | 233
[34] : | TC 34 | ℃ | 234
[35] : | TC 35 | ℃ | 235
[36] : | TC 36 | ℃ | 236
[37] : | TC 37 | ℃ | 237
[38] : | TC 38 | ℃ | 238
[39] : | TC 39 | ℃ | 239
[40] : | TC 40 | ℃ | 240
[41] : | TC 41 | ℃ | 241
[42] : | TC 42 | ℃ | 242
[43] : | TC 43 | ℃ | 243
[44] : | TC 44 | ℃ | 244
[45] : | TC 45 | ℃ | 245
[46] : | TC 46 | ℃ | 246
[47] : | TC 47 | ℃ | 247
[48] : | TC 48 | ℃ | 248
[49] : | TC 49 | ℃ | 249
[50] : | TC 50 | ℃ | 250
[51] : | TC 51 | ℃ | 251
[52] : | TC 52 | ℃ | 252
[53] : | TC 53 | ℃ | 253
[54] : | TC 54 | ℃ | 254
[55] : | TC 55 | ℃ | 255
[56] : | TC 56 | ℃ | 256
[57] : | TC 57 | ℃ | 257
[58] : | TC 58 | ℃ | 258
[59] : | TC 59 | ℃ | 259
[60] : | TC 60 | ℃ | 260
LG-P14-ID.B-TC |  |  |  | LG Electronics |  | A4(210mm*297mm)

## OD TC
THERMOCOUPLE DATA SHEET
Company |  |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  |  | Exp. Device
Model (1) |  |  |  |  | Refrigerant
Serial No. (1) |  |  |  |  | Ref. Charge
Model (2) |  |  |  |  | Test Date |  | 2018-09-06 11:08:02
Serial No. (2) |  |  |  |  | File Name
Model (3) / Serial No. (3) |  |  | / |  | -
Indoor Side Test Condition |  |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  |  | 27.00 / 19.00 ℃ |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  |  | Cooling, Indoor |  | Test Record |  | Outdoor
Memo
Thermocouple |  |  | Current | 1 min
Outdoor Side
[01] : | TC 01 | ℃ | 301
[02] : | TC 02 | ℃ | 302
[03] : | TC 03 | ℃ | 303
[04] : | TC 04 | ℃ | 304
[05] : | TC 05 | ℃ | 305
[06] : | TC 06 | ℃ | 306
[07] : | TC 07 | ℃ | 307
[08] : | TC 08 | ℃ | 308
[09] : | TC 09 | ℃ | 309
[10] : | TC 10 | ℃ | 310
[11] : | TC 11 | ℃ | 311
[12] : | TC 12 | ℃ | 312
[13] : | TC 13 | ℃ | 313
[14] : | TC 14 | ℃ | 314
[15] : | TC 15 | ℃ | 315
[16] : | TC 16 | ℃ | 316
[17] : | TC 17 | ℃ | 317
[18] : | TC 18 | ℃ | 318
[19] : | TC 19 | ℃ | 319
[20] : | TC 20 | ℃ | 320
[21] : | TC 21 | ℃ | 321
[22] : | TC 22 | ℃ | 322
[23] : | TC 23 | ℃ | 323
[24] : | TC 24 | ℃ | 324
[25] : | TC 25 | ℃ | 325
[26] : | TC 26 | ℃ | 326
[27] : | TC 27 | ℃ | 327
[28] : | TC 28 | ℃ | 328
[29] : | TC 29 | ℃ | 329
[30] : | TC 30 | ℃ | 330
[31] : | TC 31 | ℃ | 331
[32] : | TC 32 | ℃ | 332
[33] : | TC 33 | ℃ | 333
[34] : | TC 34 | ℃ | 334
[35] : | TC 35 | ℃ | 335
[36] : | TC 36 | ℃ | 336
[37] : | TC 37 | ℃ | 337
[38] : | TC 38 | ℃ | 338
[39] : | TC 39 | ℃ | 339
[40] : | TC 40 | ℃ | 340
[41] : | TC 41 | ℃ | 341
[42] : | TC 42 | ℃ | 342
[43] : | TC 43 | ℃ | 343
[44] : | TC 44 | ℃ | 344
[45] : | TC 45 | ℃ | 345
[46] : | TC 46 | ℃ | 346
[47] : | TC 47 | ℃ | 347
[48] : | TC 48 | ℃ | 348
[49] : | TC 49 | ℃ | 349
[50] : | TC 50 | ℃ | 350
[51] : | TC 51 | ℃ | 351
[52] : | TC 52 | ℃ | 352
[53] : | TC 53 | ℃ | 353
[54] : | TC 54 | ℃ | 354
[55] : | TC 55 | ℃ | 355
[56] : | TC 56 | ℃ | 356
[57] : | TC 57 | ℃ | 357
[58] : | TC 58 | ℃ | 358
[59] : | TC 59 | ℃ | 359
[60] : | TC 60 | ℃ | 360
LG-P14-OD-TC |  |  |  | LG Electronics |  | A4(210mm*297mm)

## Raw Data (hidden)
File Name
Test Date
Test Start time
Test End time
ID1 DB & WB
ID1 Test Record
OD DB & WB
OD Test Record
ID2 DB & WB
ID2 Test Record
OD DB & WB
OD Test Record
ID DB & WB
ID Test Record
OD DB & WB
OD Test Record
ID3 DB & WB
ID3 Test Record
OD DB & WB
OD Test Record
ID4 DB & WB
ID4 Test Record
OD DB & WB
OD Test Record
ID1 DB & WB
ID1 Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
ID2 DB & WB
ID2 Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
OD DB & WB
OD Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
ID3 DB & WB
ID3 Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
ID4 DB & WB
ID4 Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
ID DB & WB
ID Test Record
OD DB & WB
OD Test Record
Company
Test Name
Test No.
Observer
Rated Capacity
Rated Power Input
Rated EER/COP
Power Source
Maker
Model 1
Serial No. 1
Model 2
Serial No. 2
Model 3
Serial No. 3
Exp. Device
Refrigerant
Ref. Charge
Memo