## ID A #1
PSYCHROMETRIC CALORIMETER DATA SHEET
Company |  |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  |  | Exp. Device
Model (1) |  |  |  |  | Refrigerant
Serial No. (1) |  |  |  |  | Ref. Charge
Model (2) |  |  |  |  | Test Date |  | 2018-09-06 16:27:10
Serial No. (2) |  |  |  |  | File Name
Model (3) / Serial No. (3) |  | / |  |  | -
Indoor Side Test Condition |  |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Total Results |  | Average | 1 min | 2 min | 3 min
Total Capacity | kcal/h | 151492.1094 | 151492.1094 | 151492.1094 | 151492.1094
Total Power Input | W | 11005 | 11005 | 11005 | 11005
EER/COP | kcal/hW | 13.7658 | 13.7658 | 13.7658 | 13.7658
Capacity Ratio | % | 0 | 0 | 0 | 0
Power Input Ratio | % | 0 | 0 | 0 | 0
EER/COP Ratio | % | 0 | 0 | 0 | 0
Power Input (ID Unit) | W | 2751.0994 | 2751.0994 | 2751.0994 | 2751.0994
Voltage | V | 231.0999 | 231.0999 | 231.0999 | 231.0999
Current | A | 11.001 | 11.001 | 11.001 | 11.001
Frequency | Hz | 61.01 | 61.01 | 61.01 | 61.01
Power Factor | % | 91.0099 | 91.0099 | 91.0099 | 91.0099
Power Input (OD Unit) | W | 2751.4006 | 2751.4006 | 2751.4006 | 2751.4006
Voltage | V | 231.4001 | 231.4001 | 231.4001 | 231.4001
Current | A | 11.004 | 11.004 | 11.004 | 11.004
Frequency | Hz | 61.04 | 61.04 | 61.04 | 61.04
Power Factor | % | 91.04 | 91.04 | 91.04 | 91.04
Indoor Side A #1
Capacity | kcal/h | 58184.1758 | 58184.1797 | 58184.1797 | 58184.1797
Capacity Ratio | % | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 39173.8945 | 39173.8945 | 39173.8945 | 39173.8945
Latent Heat | kcal/h | 19010.2539 | 19010.2539 | 19010.2539 | 19010.2539
Sensible Heat Ratio | % | 67.3274 | 67.3274 | 67.3274 | 67.3274
Heat Leakage | kcal/h | 64 | 64 | 64 | 64
Drain Weight | kg/h | 32.3304 | 32.3304 | 32.3304 | 32.3304
Entering DB | ℃ | 27.11 | 27.11 | 27.11 | 27.11
Entering WB | ℃ | 19.11 | 19.11 | 19.11 | 19.11
Entering RH | % | 46.87 | 46.87 | 46.87 | 46.87
Leaving DB | ℃ | 11.11 | 11.11 | 11.11 | 11.11
Leaving WB | ℃ | 10.11 | 10.11 | 10.11 | 10.11
Leaving RH | % | 88.2476 | 88.2476 | 88.2476 | 88.2476
Enthalpy [Ent] | kcal/kg' | 12.9346 | 12.9346 | 12.9346 | 12.9346
Enthalpy [Lev] | kcal/kg' | 7.0483 | 7.0483 | 7.0483 | 7.0483
Humidity Ratio [Ent] | kg/kg' | 0.010551 | 0.010551 | 0.010551 | 0.010551
Humidity Ratio [Lev] | kg/kg' | 0.0072765 | 0.0072765 | 0.0072765 | 0.0072765
Specific Heat [Lev] | kcal/kg℃ | 0.24321 | 0.24321 | 0.24321 | 0.24321
Specific Volume [Lev] | ㎥/kg | 0.8089 | 0.8089 | 0.8089 | 0.8089
Air Flow [Lev] | CMM | 134.0858 | 134.0858 | 134.0858 | 134.0858
Static Pressure | mmAq | 0.11 | 0.11 | 0.11 | 0.11
Nozzle Diff. Pressure | mmAq | 25.11 | 25.11 | 25.11 | 25.11
Atmospheric Pressure | mmHg | 760 | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 12.11 | 12.11 | 12.11 | 12.11
Nozzle (100/150/150/300) |  | O,O,O,O
Outdoor Side
Entering DB | ℃ | 35.33 | 35.33 | 35.33 | 35.33
Entering WB | ℃ | 24.33 | 24.33 | 24.33 | 24.33
Entering RH | % | 40.4285 | 40.4285 | 40.4285 | 40.4285
Entering DP | ℃ | 19.9234 | 19.9234 | 19.9234 | 19.9234
LG-P14-ID.A-TD1 |  |  | LG Electronics |  |  | A4(210mm*297mm)

## ID A #2
PSYCHROMETRIC CALORIMETER DATA SHEET
Company |  |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  |  | Exp. Device
Model (1) |  |  |  |  | Refrigerant
Serial No. (1) |  |  |  |  | Ref. Charge
Model (2) |  |  |  |  | Test Date |  | 2018-09-06 16:27:10
Serial No. (2) |  |  |  |  | File Name
Model (3) / Serial No. (3) |  | / |  |  | -
Indoor Side Test Condition |  |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Total Results |  | Average | 1 min | 2 min | 3 min
Total Capacity | kcal/h | 151492.1094 | 151492.1094 | 151492.1094 | 151492.1094
Total Power Input | W | 11005 | 11005 | 11005 | 11005
EER/COP | kcal/hW | 13.7658 | 13.7658 | 13.7658 | 13.7658
Capacity Ratio | % | 0 | 0 | 0 | 0
Power Input Ratio | % | 0 | 0 | 0 | 0
EER/COP Ratio | % | 0 | 0 | 0 | 0
Power Input (ID Unit) | W | 2751.0994 | 2751.0994 | 2751.0994 | 2751.0994
Voltage | V | 231.0999 | 231.0999 | 231.0999 | 231.0999
Current | A | 11.001 | 11.001 | 11.001 | 11.001
Frequency | Hz | 61.01 | 61.01 | 61.01 | 61.01
Power Factor | % | 91.0099 | 91.0099 | 91.0099 | 91.0099
Power Input (OD Unit) | W | 2751.4006 | 2751.4006 | 2751.4006 | 2751.4006
Voltage | V | 231.4001 | 231.4001 | 231.4001 | 231.4001
Current | A | 11.004 | 11.004 | 11.004 | 11.004
Frequency | Hz | 61.04 | 61.04 | 61.04 | 61.04
Power Factor | % | 91.04 | 91.04 | 91.04 | 91.04
Indoor Side A #2
Capacity | kcal/h | 12345.1045 | 12345.1035 | 12345.1035 | 12345.1035
Capacity Ratio | % | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 8325.2734 | 8325.2734 | 8325.2734 | 8325.2734
Latent Heat | kcal/h | 4019.8279 | 4019.8279 | 4019.8279 | 4019.8279
Sensible Heat Ratio | % | 67.4378 | 67.4378 | 67.4378 | 67.4378
Heat Leakage | kcal/h | 64 | 64 | 64 | 64
Drain Weight | kg/h | 6.8364 | 6.8364 | 6.8364 | 6.8364
Entering DB | ℃ | 27.12 | 27.12 | 27.12 | 27.12
Entering WB | ℃ | 19.12 | 19.12 | 19.12 | 19.12
Entering RH | % | 46.8808 | 46.8808 | 46.8808 | 46.8808
Leaving DB | ℃ | 11.12 | 11.12 | 11.12 | 11.12
Leaving WB | ℃ | 10.12 | 10.12 | 10.12 | 10.12
Leaving RH | % | 88.2513 | 88.2513 | 88.2513 | 88.2513
Enthalpy [Ent] | kcal/kg' | 12.9424 | 12.9424 | 12.9424 | 12.9424
Enthalpy [Lev] | kcal/kg' | 7.0539 | 7.0539 | 7.0539 | 7.0539
Humidity Ratio [Ent] | kg/kg' | 0.01056 | 0.01056 | 0.01056 | 0.01056
Humidity Ratio [Lev] | kg/kg' | 0.0072817 | 0.0072817 | 0.0072817 | 0.0072817
Specific Heat [Lev] | kcal/kg℃ | 0.24321 | 0.24321 | 0.24321 | 0.24321
Specific Volume [Lev] | ㎥/kg | 0.80893 | 0.80893 | 0.80893 | 0.80893
Air Flow [Lev] | CMM | 28.3236 | 28.3236 | 28.3236 | 28.3236
Static Pressure | mmAq | 0.12 | 0.12 | 0.12 | 0.12
Nozzle Diff. Pressure | mmAq | 25.12 | 25.12 | 25.12 | 25.12
Atmospheric Pressure | mmHg | 760 | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 12.12 | 12.12 | 12.12 | 12.12
Nozzle (100/60/85/100) |  | O,O,O,O
Outdoor Side
Entering DB | ℃ | 35.33 | 35.33 | 35.33 | 35.33
Entering WB | ℃ | 24.33 | 24.33 | 24.33 | 24.33
Entering RH | % | 40.4285 | 40.4285 | 40.4285 | 40.4285
Entering DP | ℃ | 19.9234 | 19.9234 | 19.9234 | 19.9234
LG-P14-ID.A-TD2 |  |  | LG Electronics |  |  | A4(210mm*297mm)

## ID B #1
PSYCHROMETRIC CALORIMETER DATA SHEET
Company |  |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  |  | Exp. Device
Model (1) |  |  |  |  | Refrigerant
Serial No. (1) |  |  |  |  | Ref. Charge
Model (2) |  |  |  |  | Test Date |  | 2018-09-06 16:27:10
Serial No. (2) |  |  |  |  | File Name
Model (3) / Serial No. (3) |  | / |  |  | -
Indoor Side Test Condition |  |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Total Results |  | Average | 1 min | 2 min | 3 min
Total Capacity | kcal/h | 151492.1094 | 151492.1094 | 151492.1094 | 151492.1094
Total Power Input | W | 11005 | 11005 | 11005 | 11005
EER/COP | kcal/hW | 13.7658 | 13.7658 | 13.7658 | 13.7658
Capacity Ratio | % | 0 | 0 | 0 | 0
Power Input Ratio | % | 0 | 0 | 0 | 0
EER/COP Ratio | % | 0 | 0 | 0 | 0
Power Input (ID Unit) | W | 2751.0994 | 2751.0994 | 2751.0994 | 2751.0994
Voltage | V | 231.0999 | 231.0999 | 231.0999 | 231.0999
Current | A | 11.001 | 11.001 | 11.001 | 11.001
Frequency | Hz | 61.01 | 61.01 | 61.01 | 61.01
Power Factor | % | 91.0099 | 91.0099 | 91.0099 | 91.0099
Power Input (OD Unit) | W | 2751.4006 | 2751.4006 | 2751.4006 | 2751.4006
Voltage | V | 231.4001 | 231.4001 | 231.4001 | 231.4001
Current | A | 11.004 | 11.004 | 11.004 | 11.004
Frequency | Hz | 61.04 | 61.04 | 61.04 | 61.04
Power Factor | % | 91.04 | 91.04 | 91.04 | 91.04
Indoor Side B #1
Capacity | kcal/h | 56877.4961 | 56877.4961 | 56877.4961 | 56877.4961
Capacity Ratio | % | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 47530.5117 | 47530.5078 | 47530.5078 | 47530.5078
Latent Heat | kcal/h | 9346.9443 | 9346.9443 | 9346.9443 | 9346.9443
Sensible Heat Ratio | % | 83.5665 | 83.5665 | 83.5665 | 83.5665
Heat Leakage | kcal/h | 64 | 64 | 64 | 64
Drain Weight | kg/h | 15.8962 | 15.8962 | 15.8962 | 15.8962
Entering DB | ℃ | 27.21 | 27.21 | 27.21 | 27.21
Entering WB | ℃ | 19.21 | 19.21 | 19.21 | 19.21
Entering RH | % | 46.9778 | 46.9778 | 46.9778 | 46.9778
Leaving DB | ℃ | 11.21 | 11.21 | 11.21 | 11.21
Leaving WB | ℃ | 10.21 | 10.21 | 10.21 | 10.21
Leaving RH | % | 88.285 | 88.285 | 88.285 | 88.285
Enthalpy [Ent] | kcal/kg' | 13.0126 | 13.0126 | 13.0126 | 13.0126
Enthalpy [Lev] | kcal/kg' | 7.1041 | 7.1041 | 7.1041 | 7.1041
Humidity Ratio [Ent] | kg/kg' | 0.010639 | 0.010639 | 0.010639 | 0.010639
Humidity Ratio [Lev] | kg/kg' | 0.0073287 | 0.0073287 | 0.0073287 | 0.0073287
Specific Heat [Lev] | kcal/kg℃ | 0.24323 | 0.24323 | 0.24323 | 0.24323
Specific Volume [Lev] | ㎥/kg | 0.80921 | 0.80921 | 0.80921 | 0.80921
Air Flow [Lev] | CMM | 65.2429 | 65.2429 | 65.2429 | 65.2429
Static Pressure | mmAq | 0.21 | 0.21 | 0.21 | 0.21
Nozzle Diff. Pressure | mmAq | 25.21 | 25.21 | 25.21 | 25.21
Atmospheric Pressure | mmHg | 760 | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 12.21 | 12.21 | 12.21 | 12.21
Nozzle (100/125/150/150) |  | O,O,O,O
Outdoor Side
Entering DB | ℃ | 35.33 | 35.33 | 35.33 | 35.33
Entering WB | ℃ | 24.33 | 24.33 | 24.33 | 24.33
Entering RH | % | 40.4285 | 40.4285 | 40.4285 | 40.4285
Entering DP | ℃ | 19.9234 | 19.9234 | 19.9234 | 19.9234
LG-P14-ID.B-TD1 |  |  | LG Electronics |  |  | A4(210mm*297mm)

## ID B #2
PSYCHROMETRIC CALORIMETER DATA SHEET
Company |  |  |  |  | Rated Capacity |  | 0.0 kcal/h
Test Name |  |  |  |  | Rated Power Input |  | 0.0 W
Test No. |  |  |  |  | Rated EER/COP |  | 0.000 kcal/hW
Observer |  |  |  |  | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker |  |  |  |  | Exp. Device
Model (1) |  |  |  |  | Refrigerant
Serial No. (1) |  |  |  |  | Ref. Charge
Model (2) |  |  |  |  | Test Date |  | 2018-09-06 16:27:10
Serial No. (2) |  |  |  |  | File Name
Model (3) / Serial No. (3) |  | / |  |  | -
Indoor Side Test Condition |  |  |  |  | Outdoor Side Test Condition
DB & WB Temperature |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Total Results |  | Average | 1 min | 2 min | 3 min
Total Capacity | kcal/h | 151492.1094 | 151492.1094 | 151492.1094 | 151492.1094
Total Power Input | W | 11005 | 11005 | 11005 | 11005
EER/COP | kcal/hW | 13.7658 | 13.7658 | 13.7658 | 13.7658
Capacity Ratio | % | 0 | 0 | 0 | 0
Power Input Ratio | % | 0 | 0 | 0 | 0
EER/COP Ratio | % | 0 | 0 | 0 | 0
Power Input (ID Unit) | W | 2751.0994 | 2751.0994 | 2751.0994 | 2751.0994
Voltage | V | 231.0999 | 231.0999 | 231.0999 | 231.0999
Current | A | 11.001 | 11.001 | 11.001 | 11.001
Frequency | Hz | 61.01 | 61.01 | 61.01 | 61.01
Power Factor | % | 91.0099 | 91.0099 | 91.0099 | 91.0099
Power Input (OD Unit) | W | 2751.4006 | 2751.4006 | 2751.4006 | 2751.4006
Voltage | V | 231.4001 | 231.4001 | 231.4001 | 231.4001
Current | A | 11.004 | 11.004 | 11.004 | 11.004
Frequency | Hz | 61.04 | 61.04 | 61.04 | 61.04
Power Factor | % | 91.04 | 91.04 | 91.04 | 91.04
Indoor Side B #2
Capacity | kcal/h | 24085.4629 | 24085.4648 | 24085.4648 | 24085.4648
Capacity Ratio | % | 0 | 0 | 0 | 0
Sensible Heat | kcal/h | 16166.9414 | 16166.9414 | 16166.9414 | 16166.9414
Latent Heat | kcal/h | 7918.5229 | 7918.5229 | 7918.5229 | 7918.5229
Sensible Heat Ratio | % | 67.1233 | 67.1233 | 67.1233 | 67.1233
Heat Leakage | kcal/h | 64 | 64 | 64 | 64
Drain Weight | kg/h | 13.4669 | 13.4669 | 13.4669 | 13.4669
Entering DB | ℃ | 27.22 | 27.22 | 27.22 | 27.22
Entering WB | ℃ | 19.22 | 19.22 | 19.22 | 19.22
Entering RH | % | 46.9885 | 46.9885 | 46.9885 | 46.9885
Leaving DB | ℃ | 11.22 | 11.22 | 11.22 | 11.22
Leaving WB | ℃ | 10.22 | 10.22 | 10.22 | 10.22
Leaving RH | % | 88.2886 | 88.2886 | 88.2886 | 88.2886
Enthalpy [Ent] | kcal/kg' | 13.0204 | 13.0204 | 13.0204 | 13.0204
Enthalpy [Lev] | kcal/kg' | 7.1097 | 7.1097 | 7.1097 | 7.1097
Humidity Ratio [Ent] | kg/kg' | 0.010648 | 0.010648 | 0.010648 | 0.010648
Humidity Ratio [Lev] | kg/kg' | 0.0073339 | 0.0073339 | 0.0073339 | 0.0073339
Specific Heat [Lev] | kcal/kg℃ | 0.24323 | 0.24323 | 0.24323 | 0.24323
Specific Volume [Lev] | ㎥/kg | 0.80925 | 0.80925 | 0.80925 | 0.80925
Air Flow [Lev] | CMM | 55.2148 | 55.2148 | 55.2148 | 55.2148
Static Pressure | mmAq | 0.22 | 0.22 | 0.22 | 0.22
Nozzle Diff. Pressure | mmAq | 25.22 | 25.22 | 25.22 | 25.22
Atmospheric Pressure | mmHg | 760 | 760 | 760 | 760
Nozzle Inlet Temp. | ℃ | 12.22 | 12.22 | 12.22 | 12.22
Nozzle (50/200/85/100) |  | O,O,O,O
Outdoor Side
Entering DB | ℃ | 35.33 | 35.33 | 35.33 | 35.33
Entering WB | ℃ | 24.33 | 24.33 | 24.33 | 24.33
Entering RH | % | 40.4285 | 40.4285 | 40.4285 | 40.4285
Entering DP | ℃ | 19.9234 | 19.9234 | 19.9234 | 19.9234
LG-P14-ID.B-TD2 |  |  | LG Electronics |  |  | A4(210mm*297mm)

## ID A TC
THERMOCOUPLE DATA SHEET
Company | [5 empty] | Rated Capacity |  | 0.0 kcal/h
Test Name | [5 empty] | Rated Power Input |  | 0.0 W
Test No. | [5 empty] | Rated EER/COP |  | 0.000 kcal/hW
Observer | [5 empty] | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker | [5 empty] | Exp. Device
Model (1) | [5 empty] | Refrigerant
Serial No. (1) | [5 empty] | Ref. Charge
Model (2) | [5 empty] | Test Date |  | 2018-09-06 16:27:10
Serial No. (2) | [5 empty] | File Name
Model (3) / Serial No. (3) |  |  | / |  |  | -
Indoor Side Test Condition | [5 empty] | Outdoor Side Test Condition
DB & WB Temperature |  |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Thermocouple |  |  | Average | 1 min | 2 min | 3 min
Indoor Side A
[01] :
[02] :
[03] :
[04] :
[05] :
[06] : | TC-001 | ℃ | 106 | 106 | 106 | 106
[07] :
[08] :
[09] :
[10] :
[11] :
[12] :
[13] :
[14] :
[15] :
[16] :
[17] :
[18] :
[19] :
[20] :
[21] :
[22] :
[23] :
[24] :
[25] :
[26] :
[27] :
[28] :
[29] :
[30] :
[31] :
[32] :
[33] :
[34] :
[35] :
[36] :
[37] :
[38] :
[39] :
[40] :
[41] :
[42] :
[43] :
[44] :
[45] :
[46] :
[47] :
[48] :
[49] :
[50] :
[51] :
[52] :
[53] :
[54] :
[55] :
[56] :
[57] :
[58] :
[59] :
[60] :
LG-P14-ID.A-TC |  |  |  | LG Electronics |  |  | A4(210mm*297mm)

## ID B TC
THERMOCOUPLE DATA SHEET
Company | [5 empty] | Rated Capacity |  | 0.0 kcal/h
Test Name | [5 empty] | Rated Power Input |  | 0.0 W
Test No. | [5 empty] | Rated EER/COP |  | 0.000 kcal/hW
Observer | [5 empty] | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker | [5 empty] | Exp. Device
Model (1) | [5 empty] | Refrigerant
Serial No. (1) | [5 empty] | Ref. Charge
Model (2) | [5 empty] | Test Date |  | 2018-09-06 16:27:10
Serial No. (2) | [5 empty] | File Name
Model (3) / Serial No. (3) |  |  | / |  |  | -
Indoor Side Test Condition | [5 empty] | Outdoor Side Test Condition
DB & WB Temperature |  |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Thermocouple |  |  | Average | 1 min | 2 min | 3 min
Indoor Side B
[01] :
[02] :
[03] :
[04] :
[05] :
[06] :
[07] :
[08] :
[09] :
[10] : | TC-002 | ℃ | 210 | 210 | 210 | 210
[11] :
[12] :
[13] :
[14] :
[15] :
[16] :
[17] :
[18] :
[19] :
[20] :
[21] :
[22] :
[23] :
[24] :
[25] :
[26] :
[27] :
[28] :
[29] :
[30] :
[31] :
[32] :
[33] :
[34] :
[35] :
[36] :
[37] :
[38] :
[39] :
[40] :
[41] :
[42] :
[43] :
[44] :
[45] :
[46] :
[47] :
[48] :
[49] :
[50] :
[51] :
[52] :
[53] :
[54] :
[55] :
[56] :
[57] :
[58] :
[59] :
[60] :
LG-P14-ID.B-TC |  |  |  | LG Electronics |  |  | A4(210mm*297mm)

## OD TC
THERMOCOUPLE DATA SHEET
Company | [5 empty] | Rated Capacity |  | 0.0 kcal/h
Test Name | [5 empty] | Rated Power Input |  | 0.0 W
Test No. | [5 empty] | Rated EER/COP |  | 0.000 kcal/hW
Observer | [5 empty] | Power Source |  | 0V / 0A / 60Hz / 3-Phase 4-Wire
Maker | [5 empty] | Exp. Device
Model (1) | [5 empty] | Refrigerant
Serial No. (1) | [5 empty] | Ref. Charge
Model (2) | [5 empty] | Test Date |  | 2018-09-06 16:27:10
Serial No. (2) | [5 empty] | File Name
Model (3) / Serial No. (3) |  |  | / |  |  | -
Indoor Side Test Condition | [5 empty] | Outdoor Side Test Condition
DB & WB Temperature |  |  | 27.00 / 19.00 ℃ |  |  | DB & WB Temperature |  | 35.00 / 24.00 ℃
Test Record |  |  | Cooling, Indoor |  |  | Test Record |  | Outdoor
Memo
Thermocouple |  |  | Average | 1 min | 2 min | 3 min
Outdoor Side
[01] :
[02] :
[03] :
[04] :
[05] :
[06] :
[07] :
[08] :
[09] :
[10] :
[11] :
[12] :
[13] :
[14] :
[15] :
[16] : | TC-003 | ℃ | 316 | 316 | 316 | 316
[17] :
[18] :
[19] :
[20] :
[21] :
[22] :
[23] :
[24] :
[25] :
[26] :
[27] :
[28] :
[29] :
[30] :
[31] :
[32] :
[33] :
[34] :
[35] :
[36] :
[37] :
[38] :
[39] :
[40] :
[41] :
[42] :
[43] :
[44] :
[45] :
[46] :
[47] :
[48] :
[49] :
[50] :
[51] :
[52] :
[53] :
[54] :
[55] :
[56] :
[57] :
[58] :
[59] :
[60] :
LG-P14-OD-TC |  |  |  | LG Electronics |  |  | A4(210mm*297mm)

## Raw Data (hidden)
File Name
Test Date
Test Start time
Test End time
ID1 DB & WB
ID1 Test Record
OD DB & WB
OD Test Record
ID2 DB & WB
ID2 Test Record
OD DB & WB
OD Test Record
ID DB & WB
ID Test Record
OD DB & WB
OD Test Record
ID3 DB & WB
ID3 Test Record
OD DB & WB
OD Test Record
ID4 DB & WB
ID4 Test Record
OD DB & WB
OD Test Record
ID1 DB & WB
ID1 Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
ID2 DB & WB
ID2 Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
OD DB & WB
OD Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
ID3 DB & WB
ID3 Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
ID4 DB & WB
ID4 Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
L/S Temp. & Flow
L/S Test Record
H/S Temp. & Flow
H/S Test Record
ID DB & WB
ID Test Record
OD DB & WB
OD Test Record
Company
Test Name
Test No.
Observer
Rated Capacity
Rated Power Input
Rated EER/COP
Power Source
Maker
Model 1
Serial No. 1
Model 2
Serial No. 2
Model 3
Serial No. 3
Exp. Device
Refrigerant
Ref. Charge
Memo