## PLC 입력 접점 리스트-PSN
PLC MODEL / SLOT | MODUBUS | PLC 입력 (IN CARD) | PLC 출력 (OUT CARD) | ANALOG (IN/OUT CARD) | 변 수 |  | PLC -> 컴,Touch (내부접점) | 타 입 | 디바이스 | 사용여부 | 설 명 문
XGI-D24A (INCARD-1) SLOT NO.1 (P00010~P0002F) | 10016 | P00010 |  |  | Cooling Water Supply Fault |  | M00010 | BIT |  | 1
10017
| 10018 | P00012 |  |  | Air Supply Fault |  | M00012 | BIT |  | 1
| 10019 | P00013 |  |  | EMERGENCY_SW_CONTROL_PANEL_M |  | M00013 | BIT |  | 1
| 10020 | P00014 |  |  | R32 Exhaust Fan Fault |  | M00014 | BIT |  | 1
| 10021 | P00015 |  |  | Indoor Side A R32 Gas 화재경보 (1) |  | M00015 | BIT |  | 1
| 10022 | P00016 |  |  | Indoor Side A R32 Gas 화재경보 (2) |  | M00016 | BIT |  | 1
| 10023 | P00017 |  |  | Indoor Side A R32 Gas 화재경보 (3) |  | M00017 | BIT |  | 1
| 10024 | P00018 |  |  | TEST_UNIT_1_VOLT_CONTROLLER_AL_M |  | M00018 | BIT |  | 1
| 10025 | P00019 |  |  | TEST_UNIT_2_VOLT_CONTROLLER_AL_M |  | M00019 | BIT |  | 1
| 10026 | P0001A |  |  | Outdoor Side A R32 Gas 화재경보 (1) |  | M0001A | BIT |  | 1
| 10027 | P0001B |  |  | Outdoor Side A R32 Gas 화재경보 (2) |  | M0001B | BIT |  | 1
| 10028 | P0001C |  |  | Outdoor Side A R32 Gas 화재경보 (3) |  | M0001C | BIT |  | 1
| 10029 | P0001D |  |  | VACUUM_PUMP_SWITCH_M |  | M0001D | BIT |  | 1
| 10030 | P0001E |  |  | Vacuum Pump Fault |  | M0001E | BIT |  | 1
| 10031 | P0001F |  |  |  |  | M0001F |  |  | 0
| 10032 | P00020 |  |  | Outdoor Side Room Temp. Fault |  | M00020 | BIT |  | 1
| 10033 | P00021 |  |  | Outdoor Side AHU Fan Fault |  | M00021 | BIT |  | 1
| 10034 | P00022 |  |  | Outdoor Side Air Flow Fault |  | M00022 | BIT |  | 1
| 10035 | P00023 |  |  | Outdoor Side Ref.1 Fault |  | M00023 | BIT |  | 1
| 10036 | P00024 |  |  | OUTDOOR_SIDE_REF_1_LOW_PRESSURE_M |  | M00024 | BIT |  | 0
| 10037 | P00025 |  |  | Outdoor Side Ref.2 Fault |  | M00025 | BIT |  | 1
| 10038 | P00026 |  |  | OUTDOOR_SIDE_REF_2_LOW_PRESSURE_M |  | M00026 | BIT |  | 0
| 10039 | P00027 |  |  | Outdoor Side Ref.3 Fault |  | M00027 | BIT |  | 1
| 10040 | P00028 |  |  | OUTDOOR_SIDE_REF_3_LOW_PRESSURE_M |  | M00028 | BIT |  | 0
| 10041 | P00029 |  |  | Outdoor Side AHU Heater Fault |  | M00029 | BIT |  | 1
| 10042 | P0002A |  |  | Outdoor Side Room Air Sampler Fault |  | M0002A | BIT |  | 1
| 10043 | P0002B |  |  | OUTDOOR_SIDE_DB_CONTROLLER_AL1_M |  | M0002B | BIT |  | 1
| 10044 | P0002C |  |  | Indoor Side B R32 Gas 화재경보 (1) |  | M0002C | BIT |  | 0
| 10045 | P0002D |  |  | Indoor Side B R32 Gas 화재경보 (2) |  | M0002D | BIT |  | 0
| 10046 | P0002E |  |  | Indoor Side B R32 Gas 화재경보 (3) |  | M0002E | BIT |  | 0
| 10047 | P0002F |  |  | OUTDOOR_SIDE_AIR_SAMPLER_SW_M |  | M0002F | BIT |  | 0
PLC MODEL / SLOT | MODUBUS | PLC 입력 (IN CARD) | PLC 출력 (OUT CARD) | ANALOG (IN/OUT CARD) | 변 수 |  | PLC -> 컴,Touch (내부접점) | 타 입 | 디바이스 | 사용여부 | 설 명 문
XGI-D24A (INCARD-2) SLOT NO.2 (P00030~P0004F) | 10048 | P00030 |  |  | Indoor Side A Room Temp. Fault |  | M00030 | BIT |  | 1
| 10049 | P00031 |  |  | Indoor Side A AHU Fan Fault |  | M00031 | BIT |  | 1
| 10050 | P00032 |  |  | Indoor Side A Air Flow Fault |  | M00032 | BIT |  | 1
| 10051 | P00033 |  |  | Indoor Side A AHU Heater Fault |  | M00033 | BIT |  | 1
| 10052 | P00034 |  |  | Indoor Side A Exhaust Fan.1 Fault |  | M00034 | BIT |  | 1
| 10053 | P00035 |  |  | Indoor Side A Exhaust Fan.2 Fault |  | M00035 | BIT |  | 1
| 10054 | P00036 |  |  | Indoor Side A Room Air Sampler.1 Fault |  | M00036 | BIT |  | 1
| 10055 | P00037 |  |  | Indoor Side A Room Air Sampler.2 Fault |  | M00037 | BIT |  | 1
| 10056 | P00038 |  |  | Indoor Side A Code Tester Air Sampler.1 Fault |  | M00038 | BIT |  | 1
| 10057 | P00039 |  |  | Indoor Side A Code Tester Air Sampler.2 Fault |  | M00039 | BIT |  | 1
| 10058 | P0003A |  |  | INDOOR_SIDE_A_DB_CONTROLLER_AL1_M |  | M0003A | BIT |  | 1
| 10059 | P0003B |  |  |  |  | M0003B | BIT
| 10060 | P0003C |  |  | INDOOR_SIDE_A_AIR_SAMPLER_1_SW_M |  | M0003C | BIT |  | 0
| 10061 | P0003D |  |  | INDOOR_SIDE_A_AIR_SAMPLER_2_SW_M |  | M0003D | BIT |  | 0
| 10062 | P0003E |  |  | CODE_TESTER_A_AIR_SAMPLER_1_SW_M |  | M0003E | BIT |  | 0
| 10063 | P0003F |  |  | CODE_TESTER_A_AIR_SAMPLER_2_SW_M |  | M0003F | BIT |  | 0
| 10064 | P00040 |  |  | Indoor Side B Room Temp. Fault |  | M00040 | BIT |  | 1
| 10065 | P00041 |  |  | Indoor Side B AHU Fan Fault |  | M00041 | BIT |  | 1
| 10066 | P00042 |  |  | Indoor Side B Air Flow Fault |  | M00042 | BIT |  | 1
| 10067 | P00043 |  |  | Indoor Side B AHU Heater Fault |  | M00043 | BIT |  | 1
| 10068 | P00044 |  |  | Indoor Side B Exhaust Fan.1 Fault |  | M00044 | BIT |  | 1
| 10069 | P00045 |  |  | Indoor Side B Exhaust Fan.2 Fault |  | M00045 | BIT |  | 1
| 10070 | P00046 |  |  | Indoor Side B Room Air Sampler.1 Fault |  | M00046 | BIT |  | 1
| 10071 | P00047 |  |  | Indoor Side B Room Air Sampler.2 Fault |  | M00047 | BIT |  | 1
| 10072 | P00048 |  |  | Indoor Side B Code Tester Air Sampler.1 Fault |  | M00048 | BIT |  | 1
| 10073 | P00049 |  |  | Indoor Side B Code Tester Air Sampler.2 Fault |  | M00049 | BIT |  | 1
| 10074 | P0004A |  |  | INDOOR_SIDE_B_DB_CONTROLLER_AL1_M |  | M0004A | BIT |  | 1
| 10075 | P0004B |  |  |  |  | M0004B | BIT |  | 0
| 10076 | P0004C |  |  | INDOOR_SIDE_B_AIR_SAMPLER_1_SW_M |  | M0004C | BIT |  | 0
| 10077 | P0004D |  |  | INDOOR_SIDE_B_AIR_SAMPLER_2_SW_M |  | M0004D | BIT |  | 0
| 10078 | P0004E |  |  | CODE_TESTER_B_AIR_SAMPLER_1_SW_M |  | M0004E | BIT |  | 0
| 10079 | P0004F |  |  | CODE_TESTER_B_AIR_SAMPLER_2_SW_M |  | M0004F | BIT |  | 0
PLC MODEL / SLOT | MODUBUS | Touch -> PLC (내부접점) | PLC 출력 (OUT CARD) | ANALOG (IN/OUT CARD) | 변 수 | 컴 -> PLC (내부접점) | PLC -> 컴,Touch (내부접점) | MODUBUS | 디바이스 | 사용여부 | 설 명 문
OUTDOOR SIDE SWITCH & LAMP | 10160 | M00100 |  |  | Outdoor Side Operation On/Off | M0300 | M0100 | 0
| 10161 | M00101 |  |  | Outdoor Side AHU Fan On/Off | M0301 | M0101 | 1
| 10162 | M00102 |  |  | Outdoor Side Multi-V Cooling.1 On/Off | M0302 | M0102 | 2
| 10163 | M00103 |  |  | Outdoor Side Multi-V Cooling.2 On/Off | M0303 | M0103 | 3
| 10164 | M00104 |  |  | Outdoor Side Multi-V Cooling.3 On/Off | M0304 | M0104 | 4
| 10165 | M00105 |  |  | Outdoor Side Multi-V Cooling.4 On/Off | M0305 | M0105 | 5
| 10166 | M00106 |  |  | Outdoor Side Multi-V Cooling.5 On/Off | M0306 | M0106 | 6
| 10167 | M00107 |  |  | Outdoor Side Multi-V Cooling.6 On/Off | M0307 | M0107 | 7
| 10168 | M00108 |  |  | Outdoor Side Multi-V Cooling.7 On/Off | M0308 | M0108 | 8
| 10169 | M00109 |  |  | Outdoor Side Multi-V Cooling.8 On/Off | M0309 | M0109 | 9
| 10170 | M0010A |  |  | Outdoor Side Multi-V Cooling.9 On/Off | M030A | M010A | 10
| 10171 | M0010B |  |  | Outdoor Side Multi-V Heating.1 On/Off | M030B | M010B | 11
| 10172 | M0010C |  |  | Outdoor Side Multi-V Heating.2 On/Off | M030C | M010C | 12
| 10173 | M0010D |  |  | Outdoor Side Multi-V Heating.3 On/Off | M030D | M010D | 13
| 10174 | M0010E |  |  | Outdoor Side Multi-V Heating.4 On/Off | M030E | M010E | 14
| 10175 | M0010F |  |  | Outdoor Side Multi-V Heating.5 On/Off | M030F | M010F | 15
| 10176 | M00110 |  |  | Outdoor Side Multi-V Heating.6 On/Off | M0310 | M0110 | 16
| 10177 | M00111 |  |  | Outdoor Side Ref.1(15HP L) On/Off | M0311 | M0111 | 17
| 10178 | M00112 |  |  | Outdoor Side Ref.2(15HP L) On/Off | M0312 | M0112 | 18
| 10179 | M00113 |  |  | Outdoor Side Ref.3(20HP L) On/Off | M0313 | M0113 | 19
| 10180 | M00114 |  |  | Outdoor Side AHU Heater On/Off | M0314 | M0114 | 20
| 10181 | M00115 |  |  | Outdoor Side Humidifier On/Off | M0315 | M0115 | 21
| 10182 | M00116 |  |  | Outdoor Side WB/DP Select | M0316 | M0116 | 22
| 10183 | M00117 |  |  | SPARE.1 | M0317 | M0517 | 23
| 10184 | M00118 |  |  | SPARE.2 | M0318 | M0518 | 24
| 10185 | M00119 |  |  | SPARE.3 | M0319 | M0519 | 25
| 10186 | M0011A
| 10187 | M0011B
| 10188 | M00111C
| 10189 | M0011D
| 10190 | M0011E
| 10191 | M0011F
PLC MODEL / SLOT | MODUBUS | Touch -> PLC (내부접점) | PLC 출력 (OUT CARD) | ANALOG (IN/OUT CARD) | 변 수 | 컴 -> PLC (내부접점) | PLC -> 컴,Touch (내부접점) | MODUBUS | 디바이스 | 사용여부 | 설 명 문
INDOOR SIDE_A SWITCH & LAMP | 10208 | M00130 |  |  | Indoor Side A Operation On/Off | M0330 | M0130 | 48
| 10209 | M00131 |  |  | Indoor Side A AHU Fan On/Off | M0331 | M0131 | 49
| 10210 | M00132 |  |  | Indoor Side A Multi-V Cooling.1 On/Off | M0332 | M0132 | 50
| 10211 | M00133 |  |  | Indoor Side A Multi-V Cooling.2 On/Off | M0333 | M0133 | 51
| 10212 | M00134 |  |  | Indoor Side A Multi-V Cooling.3 On/Off | M0334 | M0134 | 52
| 10213 | M00135 |  |  | Indoor Side A Multi-V Cooling.4 On/Off | M0335 | M0135 | 53
| 10214 | M00136 |  |  | Indoor Side A Multi-V Heating.1 On/Off | M0336 | M0136 | 54
| 10215 | M00137 |  |  | Indoor Side A Multi-V Heating.2 On/Off | M0337 | M0137 | 55
| 10216 | M00138 |  |  | Indoor Side A Multi-V Heating.3 On/Off | M0338 | M0138 | 56
| 10217 | M00139 |  |  | Indoor Side A AHU Heater On/Off | M0339 | M0139 | 57
| 10218 | M0013A |  |  | Indoor Side A Humidifier On/Off | M033A | M013A | 58
| 10219 | M0013B |  |  | Indoor Side A Exhaust Fan.1 On/Off | M033B | M013B | 59
| 10220 | M0013C |  |  | Indoor Side A Nozzle.1-1 | M033C | M013C | 60
| 10221 | M0013D |  |  | Indoor Side A Nozzle.1-2 | M033D | M013D | 61
| 10222 | M0013E |  |  | Indoor Side A Nozzle.1-3 | M033E | M013E | 62
| 10223 | M0013F |  |  | Indoor Side A Nozzle.1-4 | M033F | M013F | 63
| 10224 | M00140 |  |  | Indoor Side A Exhaust Fan.2 On/Off | M0340 | M0140 | 64
| 10225 | M00141 |  |  | Indoor Side A Nozzle.2-1 | M0341 | M0141 | 65
| 10226 | M00142 |  |  | Indoor Side A Nozzle.2-2 | M0342 | M0142 | 66
| 10227 | M00143 |  |  | Indoor Side A Nozzle.2-3 | M0343 | M0143 | 67
| 10228 | M00144 |  |  | Indoor Side A Nozzle.2-4 | M0344 | M0144 | 68
| 10236 | M0014C |  |  | SPARE.6 | M034C | M054C | 76
| 10236 | M0014D |  |  | SPARE.7 | M034D | M054D | 77
| 10236 | M0014E |  |  | SPARE.8 | M034E | M054E | 78
| 10304 | M00190 |  |  | Indoor Side A Normal Power Test On | M0390 | M0190 | 144
| 10305 | M00191 |  |  | Indoor Side A Normal Power Test Off | M0391 | M0191 | 145
PLC MODEL / SLOT | MODUBUS | Touch -> PLC (내부접점) | PLC 출력 (OUT CARD) | ANALOG (IN/OUT CARD) | 변 수 | 컴 -> PLC (내부접점) | PLC -> 컴,Touch (내부접점) | MODUBUS | 디바이스 | 사용여부 | 설 명 문
INDOOR SIDE_B SWITCH & LAMP | 10240 | M00150 |  |  | Indoor Side B Operation On/Off | M0350 | M0150 | 80
| 10241 | M00151 |  |  | Indoor Side B AHU Fan On/Off | M0351 | M0151 | 81
| 10242 | M00152 |  |  | Indoor Side B Multi-V Cooling.1 On/Off | M0352 | M0152 | 82
| 10243 | M00153 |  |  | Indoor Side B Multi-V Cooling.2 On/Off | M0353 | M0153 | 83
| 10244 | M00154 |  |  | Indoor Side B Multi-V Cooling.3 On/Off | M0354 | M0154 | 84
| 10245 | M00155 |  |  | Indoor Side B Multi-V Cooling.4 On/Off | M0355 | M0155 | 85
| 10246 | M00156 |  |  | Indoor Side B Multi-V Cooling.5 On/Off | M0356 | M0156 | 86
| 10247 | M00157 |  |  | Indoor Side B Multi-V Cooling.6 On/Off | M0357 | M0157 | 87
| 10248 | M00158 |  |  | Indoor Side B Multi-V Heating.1 On/Off | M0358 | M0158 | 88
| 10249 | M00159 |  |  | Indoor Side B Multi-V Heating.2 On/Off | M0359 | M0159 | 89
| 10250 | M0015A |  |  | Indoor Side B Multi-V Heating.3 On/Off | M035A | M015A | 90
| 10251 | M0015B |  |  | Indoor Side B AHU Heater On/Off | M035B | M015B | 91
| 10252 | M0015C |  |  | Indoor Side B Humidifier On/Off | M035C | M015C | 92
| 10253 | M0015D |  |  | Indoor Side B Exhaust Fan.1 On/Off | M035D | M015D | 93
| 10254 | M0015E |  |  | Indoor Side B Nozzle.1-1 | M035E | M015E | 94
| 10255 | M0015F |  |  | Indoor Side B Nozzle.1-2 | M035F | M015F | 95
| 10256 | M00160 |  |  | Indoor Side B Nozzle.1-3 | M0360 | M0160 | 96
| 10257 | M00161 |  |  | Indoor Side B Nozzle.1-4 | M0361 | M0161 | 97
| 10257 | M00162 |  |  | Indoor Side B Exhaust Fan.2 On/Off | M0362 | M0162 | 98
| 10257 | M00163 |  |  | Indoor Side B Nozzle.2-1 | M0363 | M0163 | 99
| 10257 | M00164 |  |  | Indoor Side B Nozzle.2-2 | M0364 | M0164 | 100
| 10257 | M00165 |  |  | Indoor Side B Nozzle.2-3 | M0365 | M0165 | 101
| 10257 | M00166 |  |  | Indoor Side B Nozzle.2-4 | M0366 | M0166 | 102
| 10306 | M00192 |  |  | Indoor Side B Normal Power Test On | M0392 | M0192 | 146
| 10307 | M00193 |  |  | Indoor Side B Normal Power Test Off | M0393 | M0193 | 147
PLC MODEL / SLOT | MODUBUS | Touch -> PLC (내부접점) | PLC 출력 (OUT CARD) | ANALOG (IN/OUT CARD) | 변 수 | 컴 -> PLC (내부접점) | PLC -> 컴,Touch (내부접점) | MODUBUS | 디바이스 | 사용여부 | 설 명 문
VVVF_1 SWITCH & LAMP | 10272 | M00170 |  |  | VVVF.1 On | M0370 | M0170 | 112
| 10273 | M00171 |  |  | VVVF.1 Off | M0371 | M0171 | 113
| 10274 | M00172 |  |  | VVVF.1 Low Volt. Select | M0372 | M0172 | 114
| 10275 | M00173 |  |  | 50Hz Test | M0373 | M0173 | 115
| 10276 | M00174 |  |  | 60Hz Test | M0374 | M0174 | 116
| 10277 | M00175 |  |  | 1P 2W Select | M0375 | M0175 | 117
| 10278 | M00176 |  |  | 3P 3W Select | M0376 | M0176 | 118
| 10279 | M00177 |  |  | 3P 4W Select | M0377 | M0177 | 119
| 10280 | M00178 |  |  | Test Power On | M0378 | M0178 | 120
| 10281 | M00179 |  |  | Test Power Off | M0379 | M0179 | 121
PLC MODEL / SLOT | MODUBUS | Touch -> PLC (내부접점) | PLC 출력 (OUT CARD) | ANALOG (IN/OUT CARD) | 변 수 | 컴 -> PLC (내부접점) | PLC -> 컴,Touch (내부접점) | MODUBUS | 디바이스 | 사용여부 | 설 명 문
VVVF_2 SWITCH & LAMP | 10288 | M00180 |  |  | VVVF.2 On | M0380 | M0180 | 128
| 10289 | M00181 |  |  | VVVF.2 Off | M0381 | M0181 | 129
| 10290 | M00182 |  |  | VVVF.2 Low Volt. Select | M0382 | M0182 | 130
| 10291 | M00183 |  |  | 50Hz Test | M0383 | M0183 | 131
| 10292 | M00184 |  |  | 60Hz Test | M0384 | M0184 | 132
| 10293 | M00185 |  |  | 1P 2W Select | M0385 | M0185 | 133
| 10294 | M00186 |  |  | 3P 3W Select | M0386 | M0186 | 134
| 10295 | M00187 |  |  | 3P 4W Select | M0387 | M0187 | 135
| 10296 | M00188 |  |  | Test Power On | M0388 | M0188 | 136
| 10297 | M00189 |  |  | Test Power Off | M0389 | M0189 | 137
PLC MODEL / SLOT | MODUBUS | Touch -> PLC (내부접점) | PLC 출력 (OUT CARD) | ANALOG (IN/OUT CARD) | 변 수 | 컴 -> PLC (내부접점) | PLC -> 컴,Touch (내부접점) | MODUBUS | 디바이스 | 사용여부 | 설 명 문
Ohters SWITCH & LAMP | 10500 | M00600 |  |  | TOTAL_ALARM
| 10501 | M01170 |  |  | BUZZER_STOP | M0593 | M0590
| 10502 | M01171 |  |  | ALARM_RESET | - | M0591